SCOPE OF WORK
Sewer Ejector Pit Cleaning & Discharge Piping Replacement
Paramus Veterans Memorial Home
New Jersey Department of Veterans Affairs

1. PROJECT OVERVIEW
The Contractor shall furnish all labor, supervision, materials, equipment, tools, transportation, disposal, permits, confined space entry services, bypass pumping, testing, startup, and incidentals necessary to provide a complete sewer ejector pit cleaning and discharge piping replacement project.

The completed system shall be fully operational upon completion of the work.

2. EXISTING CONDITIONS
The existing sewer ejector pit contains duplex submersible sewage ejector pumps discharging through existing 4-inch discharge piping equipped with isolation valves and check valves. Existing piping components have reached the end of their service life and require replacement. The work includes cleaning accumulated wastewater solids and replacing the discharge piping from the pump discharge connections to the existing discharge piping outside the pit limits.

The contractor shall verify all existing field conditions prior to bidding.

The attached sewer ejector detail is provided for reference only. The contractor shall verify all dimensions, piping configurations, and existing conditions before commencing work.

3. SCOPE OF SERVICES
3.1 Sewer Ejector Pit Cleaning
The Contractor shall:
· Mobilize personnel and equipment.
· Establish all required safety barriers.
· Clean the pit using a minimum 4,000 PSI high-pressure jetting system.
· Remove grease, sludge, sediment, debris, and accumulated solids.
· Utilize a vacuum/vactor truck to remove wastewater and debris.
· Provide bypass pumping as necessary to maintain uninterrupted building operations.
· Dispose of all waste in accordance with Federal, State, and local regulations.

3.2 Confined Space Entry
The Contractor shall provide:
· Confined space permits
· Atmospheric monitoring
· Rescue equipment
· Rescue personnel
· Ventilation equipment
· Fall protection
· Communication equipment
All confined space work shall comply with OSHA requirements.

3.3 Removal of Existing Piping
The Contractor shall:
· Isolate the sewer ejector system.
· Remove existing discharge piping.
· Remove both existing check valves.
· Remove both existing isolation valves.
· Remove all fittings, supports, hardware, flanges, gaskets, and appurtenances required for replacement.
All removed material shall become property of the Contractor.

3.4 Installation of New Discharge Piping
The Contractor shall furnish and install:
· New 4-inch discharge piping
· Two (2) new 4-inch isolation valves
· Two (2) new 4-inch check valves
· Galvanized steel pipe or copper ProPress piping
· All elbows
· Couplings
· Flanges
· Supports
· Anchors
· Bolts
· Nuts
· Gaskets
· Pipe supports
· Miscellaneous hardware

The Contractor shall reconnect the new piping to:
· Existing pump discharge connections
· Existing discharge piping outside the pit

All piping shall be:
· Properly aligned
· Properly supported
· Installed per manufacturer recommendations
· Installed in accordance with applicable plumbing and mechanical codes

3.5 Testing and Startup
The Contractor shall:
· Inspect all installations.
· Test all joints for leakage.
· Operate both sewer ejector pumps.
· Verify proper operation of:
· Check valves
· Isolation valves
· Pump discharge piping
Any deficiencies identified during testing shall be corrected at no additional cost.

4. PERFORMANCE REQUIREMENTS
The completed installation shall:
· Be leak free.
· Be fully operational.
· Maintain uninterrupted wastewater conveyance.
· Meet all applicable plumbing and mechanical codes.
· Meet OSHA safety requirements.
· Be installed in a neat and professional manner.

5. CONTRACTOR RESPONSIBILITIES
The Contractor shall include:
· Labor
· Materials
· Equipment
· Confined space entry
· Disposal
· Testing
· Startup
· Cleanup
· Bypass pumping
· Temporary protections
Any work necessary for a complete operational installation shall be included whether specifically identified or not.

6. DELIVERABLES
The Contractor shall provide:
· Complete sewer ejector pit cleaning.
· Disposal manifests upon request.
· New discharge piping system.
· New isolation valves.
· New check valves.
· Testing documentation.
· Startup verification.
· Final cleanup of the work area.








The below sewer ejector detail is provided for informational purposes only. The Contractor shall field verify all dimensions, piping layouts, equipment, and existing conditions prior to bidding. The Contractor shall be responsible for all measurements and coordination necessary to provide a complete and operational installation."
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