## READ ME - Instructions
Introduction
This is a supplemental tool to collect data during environmental Legionella sampling. The sample collector must adhere to the New Jersey Department of Health's Environmental Sampling and Testing Guidance when collecting environmental samples for Legionella testing. That guidance is available within the Legionellosis Communicable Disease Manual Chapter located at https://www.nj.gov/health/cd/topics/legion.shtml. The below instructions are for recording data on the Sampling Data Sheet. The completed Sampling Data Sheet should be submitted to the Local Health Department in addition to the chain of custody and original test result report(s) provided by the laboratory.
Last updated: November 2024
Instructions
1. Review the Data Dictionary to become familiar with the different types of variables collected in this database.
2. Assign a unique sample identification number for each sample. Labels with pre-assigned IDs may be printed ahead of time for the sample bottles.
3. Complete the sample location variables, including the floor number, room number or area, and fixture type (e.g., sink, showerhead, water heater drain valve). Assign a unique sample location ID to this specific sample location.
4. Specify whether the sample is potable hot water, potable cold water, non-potable water, or a biofilm swab.
5. Specify the sample volume. For investigative sampling in response to a case of Legionnaires' disease, the sample volume must be 1000 mL.
6. Specify whether the sample was a first-draw or post-flush water sample (or non-applicable for biofilm swabs). All potable hot water samples should be first-draw unless otherwise directed by public health authorities.
7. Record first-draw water quality parameters, including temperature, pH, and disinfectant residual (e.g., free chlorine). Use a calibrated digital colorimeter for measuring disinfectant residual. Test kits and color wheels are not recommended for potable water samples.
8. Record the time (in seconds) it takes for the hot water to reach its maximum temperature. Further investigate locations where it takes more than a minute for the water to reach its maximum temperature.
9. Record post-flush water quality parameters, including temperature, pH, and disinfectant residual (e.g., free chlorine).
10. Indicate whether the Legionella culture test result was positive (Legionella detected) or negative (Legionella not detected). In some instances, "pending" or "not tested" are appropriate responses (for example, if a sample was damaged in transit).
11. If the sample was positive, specify the Legionella species and serogroup identified.
12. Record the Legionella concentration in colony forming units (CFU) per milliliter (mL).
13. Document any notes or observations regarding the sample. For example, if it was a sink in a room that was vacant for an extended period of time, or if there was discoloration of the water.
14. If Legionella is detected, or if water quality parameters fall outside acceptable ranges, take corrective actions to investigate the root cause. Document the control measures implemented to address the Legionella detection and/or the out-of-range water quality parameters.

## Data Dictionary
Data Dictionary
Variable | Description | Example
E-Number | Unique identification code assigned to the investigation by DOH | E-235-2024
Sample ID | Identification code of a specific sample assigned by sampler or analyzing laboratory | NJ0101-2024
Sample Date/Time | Sample collection date and time | 01/01/24 01:15PM
Sample Location ID | Unique identification code assigned to sample location/fixture - must be consistent in all sampling events | Room130_KitchenSink_Flushed_Cold
Sample Location Floor | Floor number of collected sample | Floor 6, basement
Sample Location Room/Area | Room number or area of collected sample | Room 130, medication prep room, mechanical room
Sample Location Fixture | Description of sampled fixture | Sink, showerhead, fountain, water heater drain valve
Sample Type | Select type of sample collected from drop-down list | Potable Hot Water/Potable Cold Water/Non-Potable Water/Biofilm Swab
Sample Volume | Volume of collected sample | 1000 mL
Sample Collection | Select whether the sample was collected on first draw or post flush from drop-down list | First Draw/Post Flush/Not Applicable
Pre-Flush Temp | Temperature of first-draw water sample | 110.3 F
Pre-Flush pH | pH value of first-draw water sample | 7.65
Pre-Flush Disinfectant Residual | Disinfectant residual of first-draw water sample | 0.21 (mg/L) free chlorine
Time to Achieve Steady State Temp | Time (in seconds) to reach maximum water temperature | 15 seconds
Post-Flush Temp | Temperature of post-flush water sample | 120.5 F
Post-Flush pH | pH value of post-flush water sample | 7.6
Post-Flush Disinfectant Residual | Disinfectant residual of post-flush water sample | 0.50 (mg/L) free chlorine
Legionella Culture Result | Whether Legionella was detected by culture methods | Positive/Not Detected/Pending/Not Tested
Legionella Species Identification | Species/serogroup detected | Legionella pneumophila serogroup 1
Legionella Concentration | Number of colony-forming units (CFUs) per mL detected | 3.5 CFU/mL
Notes | Any notes or observations regarding the sample location | Room 114 inaccessible, sampled room 214 instead (downstream connection on riser)
Corrective Action Findings | Take corrective actions to investigate the root cause and document the findings (e.g., identified factors supporting growth) | Upon review, showerhead was not routinely flushed and there was evidence of biofilm/scale build-up
Implemented Control Measure | Planned or implemented control measure to address Legionella detections and inadequate water quality | Replaced showerhead and added to flushing program
Control Measure Date | Date control measure was implemented | 2024-01-15

## Sampling Data Sheet
Environmental Legionella Sampling Data Sheet
E-Number | Sample ID | Sample Date/Time | Sample Location ID | Sample Location Floor | Sample Location Room/Area | Sample Location Fixture | Sample Type | Sample Volume | Sample Collection | Pre-Flush Temp | Pre-Flush pH | Pre-Flush Disinfectant Residual | Time to Achieve Steady State Temp | Post-Flush Temp | Post-Flush pH | Post-Flush Disinfectant Residual | Legionella Culture Result | Legionella Species Identification | Legionella Concentration | Notes | Corrective Action Findings | Implemented Control Measure | Control Measure Date
|  | (MM/DD/YY and HH:MM) | [5 empty] | (mL) | (Select from Dropdown list) | (°F) |  | (mg/L) | (seconds) | (°F) |  | (mg/L) | (Select from Dropdown list) |  | (CFU/mL)